## VARIO2
Rev 18.0
Select Power Supply Output Voltage to be used
FALSE
Voltage Drop On Cable
PSU Output Voltage (V) | 24 | V
PSU O/P Power (W) |  | W
Cable Voltage Drop | 2 | V
| Lamp Type : - | i2 / w2 | i4 | i6 / w4 | i8 / w8 | i16 / w16
| Lamp Power (W): - | 12 | 13 | 25 | 46 | 100
| Current in the Cable (A): - | 0.54545 | 0.59091 | 1.1364 | 2.0909 | 4.5455
| Cable Losses (W): - | 1.0909 | 1.1818 | 2.2727 | 4.1818 | 9.0909 | Warning : - Are these cable losses acceptable?
| Output Power Required from PSU (Watts): - | 13.0909 | 14.1818 | 27.2727 | 50.1818 | 109.0909
| Cable loss as a % of lamp power | 9.091% | 9.091% | 9.091% | 9.091% | 9.091% | #REF!
Nominal Wire Cross Section - (mm2) | Total 2-Core Cable Resistance - (Ohms/m) | Max Cable Runs (m)
0.33 | 0.108 | 33.9506 | 31.339 | 16.2963 | 8.8567 | 4.0741
0.5 | 0.072 | 50.9259 | 47.0085 | 24.4444 | 13.285 | 6.1111
0.75 | 0.049 | 74.8299 | 69.0738 | 35.9184 | 19.5209 | 8.9796
0.82 | 0.042 | 87.3016 | 80.5861 | 41.9048 | 22.7743 | 10.4762
1 | 0.0362 | 101.2891 | 93.4977 | 48.6188 | 26.4233 | 12.1547
1.5 | 0.0242 | 151.5152 | 139.8601 | 72.7273 | 39.5257 | 18.1818
2.5 | 0.01482 | 247.4134 | 228.3816 | 118.7584 | 64.5426 | 29.6896
4 | 0.0098 | 374.1497 | 345.3689 | 179.5918 | 97.6043 | 44.898
Nominal Wire AWG | Total 2-Core Cable Resistance - (Ohms/ft) | Max Cable Runs (ft)
22 | 0.033 | 111.1111 | 102.5641 | 53.3333 | 28.9855 | 13.3333
20 | 0.021 | 174.6032 | 161.1722 | 83.8095 | 45.5487 | 20.9524
18 | 0.013 | 282.0513 | 260.355 | 135.3846 | 73.5786 | 33.8462
16 | 0.008 | 458.3333 | 423.0769 | 220 | 119.5652 | 55
14 | 0.005 | 733.3333 | 676.9231 | 352 | 191.3043 | 88
12 | 0.003 | 1222.2222 | 1128.2051 | 586.6667 | 318.8406 | 146.6667
10 | 0.002 | 1833.3333 | 1692.3077 | 880 | 478.2609 | 220
Note on C3: Power Supply Voltage Enter the Power Supply Output voltage you intend to use with the product.
Note on C11: Cable Voltage Drop The maximum voltage drop that can be tolerated across the cable is the Power Supply voltage minus the minimum input voltage of the lamp, this can lead to large power losses in the cable which is undesirable. We therefore strongly recommend that the voltage drops are kept to a minimum. The default has been set to 2 Volts. Larger drops and therefore higher losses maybe acceptable in your system. But you must consider the size of the PSU required, the heat being dissipated within the cable etc. Changes to the Cable Voltage Drop can only be made when "Advanced Settings" are selected. If in doubt please call Raytec for assistance.

## VARIO
Rev 18.0
Select Power Supply Output Voltage to be used
FALSE
Voltage Drop On Cable
PSU Output Voltage (V) | 24 | V
PSU O/P Power (W) |  | W
Cable Voltage Drop | 2 | V
| Lamp Type : - | i2 / w2 | i4 / w4 | i8 / w8
| Lamp Power (W): - | 12 | 24 | 48
| Current in the Cable (A): - | 0.54545 | 1.0909 | 2.1818
| Cable Losses (W): - | 1.0909 | 2.1818 | 4.3636 | Warning : - Are these cable losses acceptable?
| Output Power Required from PSU (Watts): - | 13.0909 | 26.1818 | 52.3636
| Cable loss as a % of lamp power | 9.091% | 9.091% | 9.091% | #REF!
Nominal Wire Cross Section - (mm2) | Total 2-Core Cable Resistance - (Ohms/m) | Max Cable Runs (m)
0.33 | 0.108 | 33.9506 | 16.9753 | 8.4877
0.5 | 0.072 | 50.9259 | 25.463 | 12.7315
0.75 | 0.049 | 74.8299 | 37.415 | 18.7075
0.82 | 0.042 | 87.3016 | 43.6508 | 21.8254
1 | 0.0362 | 101.2891 | 50.6446 | 25.3223
1.5 | 0.0242 | 151.5152 | 75.7576 | 37.8788
2.5 | 0.01482 | 247.4134 | 123.7067 | 61.8534
4 | 0.0098 | 374.1497 | 187.0748 | 93.5374
Nominal Wire AWG | Total 2-Core Cable Resistance - (Ohms/ft) | Max Cable Runs (ft)
22 | 0.033 | 111.1111 | 55.5556 | 27.7778
20 | 0.021 | 174.6032 | 87.3016 | 43.6508
18 | 0.013 | 282.0513 | 141.0256 | 70.5128
16 | 0.008 | 458.3333 | 229.1667 | 114.5833
14 | 0.005 | 733.3333 | 366.6667 | 183.3333
12 | 0.003 | 1222.2222 | 611.1111 | 305.5556
10 | 0.002 | 1833.3333 | 916.6667 | 458.3333
Note on C3: Power Supply Voltage Enter the Power Supply Output voltage you intend to use with the product.
Note on C11: Cable Voltage Drop The maximum voltage drop that can be tolerated across the cable is the Power Supply voltage minus the minimum input voltage of the lamp, this can lead to large power losses in the cable which is undesirable. We therefore strongly recommend that the voltage drops are kept to a minimum. The default has been set to 2 Volts. Larger drops and therefore higher losses maybe acceptable in your system. But you must consider the size of the PSU required, the heat being dissipated within the cable etc. Changes to the Cable Voltage Drop can only be made when "Advanced Settings" are selected. If in doubt please call Raytec for assistance.

## Raymax & Raylux
Rev 18.0
Cable length calculations
Tables show max allowable distances from PSU to lamp and cable drop per unit distance
to ensure lamp runs at maximum performance
| Section 1: Max distance - Metric cables sizes |  | Section 3: Voltage drop per metre of cable - Metric cable
| Section 2: Max distance - AWG cable sizes |  | Section 4: Voltage drop per foor of cable - AWG cable sizes
Important Notes:
All models (except 25) are for twin panel, AI systems.
For AI systems - assumes both supply cables are extended. If supply cables commoned - then achievable distances will be halved.
| RM/RL300 same as equivalent RM/RL200 |  | RM/RL150 same as equivalent RM/RL 100
For Hybrid models, use same distance as equivalent IR and WL models
|  |  | MAXIMUM CABLE RUNS | [5 empty] | VOLTAGE DROP PER UNIT DISTANCE OF CABLE
| RAYMAX - Infra-Red - Standard |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI | RAYMAX - Infra-Red - Standard |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI
|  |  | Per Panel - amps: | 1 Panel @ 0.5 | 2 Panels @ 0.5 | 2 Panels @ 1.2 | 2 Panels @ 2.2 | 3 Panels @ 2.2 |  |  | Per Panel - amps: | 1 Panel @ 0.5 | 2 Panels @ 0.5 | 2 Panels @ 1.2 | 2 Panels @ 2.2 | 3 Panels @ 2.2
| Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.5 | 1 | 2.4 | 4.4 | 6.6 | Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.5 | 1 | 2.4 | 4.4 | 6.6
| Cross Section - mm | Resistance - Ohms/m |  |  | Max Cable Runs - metres |  |  |  | Cross Section - mm | Resistance - Ohms/m |  |  | Voltage drop per metre - maximum voltage drop allowed = 1V
| 0.5 | 0.072 |  | 27.7778 | 27.7778 | 11.5741 | 6.3131 | 6.3131 | 0.5 | 0.072 |  | 0.036 | 0.036 | 0.0864 | 0.1584 | 0.1584
| 0.75 | 0.049 |  | 40.8163 | 40.8163 | 17.0068 | 9.2764 | 9.2764 | 0.75 | 0.049 |  | 0.0245 | 0.0245 | 0.0588 | 0.1078 | 0.1078
| 1 | 0.0362 |  | 55.2486 | 55.2486 | 23.0203 | 12.5565 | 12.5565 | 1 | 0.0362 |  | 0.0181 | 0.0181 | 0.04344 | 0.07964 | 0.07964
| 1.5 | 0.0242 |  | 82.6446 | 82.6446 | 34.4353 | 18.7829 | 18.7829 | 1.5 | 0.0242 |  | 0.0121 | 0.0121 | 0.02904 | 0.05324 | 0.05324
| 2.5 | 0.01482 |  | 134.9528 | 134.9528 | 56.2303 | 30.6711 | 30.6711 | 2.5 | 0.01482 |  | 0.00741 | 0.00741 | 0.017784 | 0.032604 | 0.032604
| 4 | 0.0098 |  | 204.0816 | 204.0816 | 85.034 | 46.3822 | 46.3822 | 4 | 0.0098 |  | 0.0049 | 0.0049 | 0.01176 | 0.02156 | 0.02156
| RAYMAX - Infra-Red - Covert | [7 empty] | RAYMAX - Infra-Red - Covert
| RAYMAX - Infra-Red - Platinum | [7 empty] | RAYMAX - Infra-Red - Platinum
| RAYMAX - Infra-Red - 10 degree verions |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI | RAYMAX - Infra-Red - 10 degree verions |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI
|  |  | Per Panel - amps: | 1 Panel @ 1 | 2 Panels @ 1 | 2 Panels @ 2 | 2 Panels @ 3 | 3 Panels @ 3 |  |  | Per Panel - amps: | 1 Panel @ 1 | 2 Panels @ 1 | 2 Panels @ 2 | 2 Panels @ 3 | 3 Panels @ 3
| Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 1 | 2 | 4 | 6 | 9 | Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 1 | 2 | 4 | 6 | 9
| Cross Section - mm | Resistance - Ohms/m |  |  | Max Cable Runs - metres |  |  |  | Cross Section - mm | Resistance - Ohms/m |  |  | Voltage drop per metre - maximum voltage drop allowed = 1V
| 0.5 | 0.072 |  | 13.8889 | 13.8889 | 6.9444 | 4.6296 | 4.6296 | 0.5 | 0.072 |  | 0.072 | 0.072 | 0.144 | 0.216 | 0.216
| 0.75 | 0.049 |  | 20.4082 | 20.4082 | 10.2041 | 6.8027 | 6.8027 | 0.75 | 0.049 |  | 0.049 | 0.049 | 0.098 | 0.147 | 0.147
| 1 | 0.0362 |  | 27.6243 | 27.6243 | 13.8122 | 9.2081 | 9.2081 | 1 | 0.0362 |  | 0.0362 | 0.0362 | 0.0724 | 0.1086 | 0.1086
| 1.5 | 0.0242 |  | 41.3223 | 41.3223 | 20.6612 | 13.7741 | 13.7741 | 1.5 | 0.0242 |  | 0.0242 | 0.0242 | 0.0484 | 0.0726 | 0.0726
| 2.5 | 0.01482 |  | 67.4764 | 67.4764 | 33.7382 | 22.4921 | 22.4921 | 2.5 | 0.01482 |  | 0.01482 | 0.01482 | 0.02964 | 0.04446 | 0.04446
| 4 | 0.0098 |  | 102.0408 | 102.0408 | 51.0204 | 34.0136 | 34.0136 | 4 | 0.0098 |  | 0.0098 | 0.0098 | 0.0196 | 0.0294 | 0.0294
| RAYLUX - White-Light - All versions |  | Lamp Current | RL25 | RL50-AI | RL100-AI | RL200-AI | RL300-AI | RAYLUX - White-Light - All versions |  | Lamp Current | RL25 | RL50-AI | RL100-AI | RL200-AI | RL300-AI
|  |  | Per Panel - amps: | 1 Panel @ 0.7 | 2 Panels @ 0.7 | 2 Panels @ 1.4 | 2 Panels @ 2.1 | 3 Panels @ 2.1 |  |  | Per Panel - amps: | 1 Panel @ 0.7 | 2 Panels @ 0.7 | 2 Panels @ 1.4 | 2 Panels @ 2.1 | 3 Panels @ 2.1
| Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.7 | 1.4 | 2.8 | 4.2 | 6.3 | Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.7 | 1.4 | 2.8 | 4.2 | 6.3
| Cross Section - mm | Resistance - Ohms/m |  |  | Max Cable Runs - metres |  |  |  | Cross Section - mm | Resistance - Ohms/m |  |  | Voltage drop per metre - maximum voltage drop allowed = 0.6V
| 0.5 | 0.072 |  | 11.9048 | 11.9048 | 5.9524 | 3.9683 | 3.9683 | 0.5 | 0.072 |  | 0.0504 | 0.0504 | 0.1008 | 0.1512 | 0.1512
| 0.75 | 0.049 |  | 17.4927 | 17.4927 | 8.7464 | 5.8309 | 5.8309 | 0.75 | 0.049 |  | 0.0343 | 0.0343 | 0.0686 | 0.1029 | 0.1029
| 1 | 0.0362 |  | 23.678 | 23.678 | 11.839 | 7.8927 | 7.8927 | 1 | 0.0362 |  | 0.02534 | 0.02534 | 0.05068 | 0.07602 | 0.07602
| 1.5 | 0.0242 |  | 35.4191 | 35.4191 | 17.7096 | 11.8064 | 11.8064 | 1.5 | 0.0242 |  | 0.01694 | 0.01694 | 0.03388 | 0.05082 | 0.05082
| 2.5 | 0.01482 |  | 57.8369 | 57.8369 | 28.9184 | 19.279 | 19.279 | 2.5 | 0.01482 |  | 0.010374 | 0.010374 | 0.020748 | 0.031122 | 0.031122
| 4 | 0.0098 |  | 87.4636 | 87.4636 | 43.7318 | 29.1545 | 29.1545 | 4 | 0.0098 |  | 0.00686 | 0.00686 | 0.01372 | 0.02058 | 0.02058
There are internal adjustments available within the PSU to increase the above distances by upto 50%.
Contact Raytec technical support for advice.
| UK/Europe/Middle East | +44 (0) 1670 520 055 | Americas | + 1 613 270 9990
| RAYMAX - Infra-Red - Standard |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI | RAYMAX - Infra-Red - Standard |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI
|  |  | Per Panel - amps: | 1 Panel @ 0.5 | 2 Panels @ 0.5 | 2 Panels @ 1.2 | 2 Panels @ 2.2 | 3 Panels @ 2.2 |  |  | Per Panel - amps: | 1 Panel @ 0.5 | 2 Panels @ 0.5 | 2 Panels @ 1.2 | 2 Panels @ 2.2 | 3 Panels @ 2.2
| Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.5 | 1 | 2.4 | 4.4 | 6.6 | Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.5 | 1 | 2.4 | 4.4 | 6.6
| AWG | Resistance - Ohms/ft |  |  | Max Cable Runs - feet |  |  |  | AWG | Resistance - Ohms/ft |  |  | Voltage drop per foot - maximum voltage drop allowed = 1V
| 20 | 0.0207 |  | 96.6184 | 96.6184 | 40.2576 | 21.9587 | 21.9587 | 20 | 0.0207 |  | 0.01035 | 0.01035 | 0.02484 | 0.04554 | 0.04554
| 18 | 0.01302 |  | 153.6098 | 153.6098 | 64.0041 | 34.9113 | 34.9113 | 18 | 0.01302 |  | 0.00651 | 0.00651 | 0.015624 | 0.028644 | 0.028644
| 16 | 0.008128 |  | 246.063 | 246.063 | 102.5262 | 55.9234 | 55.9234 | 16 | 0.008128 |  | 0.004064 | 0.004064 | 0.0097536 | 0.017882 | 0.017882
| 14 | 0.00515 |  | 388.3495 | 388.3495 | 161.8123 | 88.2613 | 88.2613 | 14 | 0.00515 |  | 0.002575 | 0.002575 | 0.00618 | 0.01133 | 0.01133
| 13 | 0.004084 |  | 489.716 | 489.716 | 204.0483 | 111.2991 | 111.2991 | 13 | 0.004084 |  | 0.002042 | 0.002042 | 0.0049008 | 0.0089848 | 0.0089848
| 11 | 0.002568 |  | 778.8162 | 778.8162 | 324.5067 | 177.0037 | 177.0037 | 11 | 0.002568 |  | 0.001284 | 0.001284 | 0.0030816 | 0.0056496 | 0.0056496
| RAYMAX - Infra-Red - Covert | [7 empty] | RAYMAX - Infra-Red - Covert
| RAYMAX - Infra-Red - Platinum | [7 empty] | RAYMAX - Infra-Red - Platinum
| RAYMAX - Infra-Red - 10 degree verions |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI | RAYMAX - Infra-Red - 10 degree verions |  | Lamp Current | RM25 | RM50-AI | RM100-AI | RM200-AI | RM300-AI
|  |  | Per Panel - amps: | 1 Panel @ 1 | 2 Panels @ 1 | 2 Panels @ 2 | 2 Panels @ 3 | 3 Panels @ 3 |  |  | Per Panel - amps: | 1 Panel @ 1 | 2 Panels @ 1 | 2 Panels @ 2 | 2 Panels @ 3 | 3 Panels @ 3
| Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 1 | 2 | 4 | 6 | 9 | Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 1 | 2 | 4 | 6 | 9
| AWG | Resistance - Ohms/ft |  |  | Max Cable Runs - feet |  |  |  | AWG | Resistance - Ohms/ft |  |  | Voltage drop per foot - maximum voltage drop allowed = 1V
| 20 | 0.0207 |  | 48.3092 | 48.3092 | 24.1546 | 16.1031 | 16.1031 | 20 | 0.0207 |  | 0.0207 | 0.0207 | 0.0414 | 0.0621 | 0.0621
| 18 | 0.01302 |  | 76.8049 | 76.8049 | 38.4025 | 25.6016 | 25.6016 | 18 | 0.01302 |  | 0.01302 | 0.01302 | 0.02604 | 0.03906 | 0.03906
| 16 | 0.008128 |  | 123.0315 | 123.0315 | 61.5157 | 41.0105 | 41.0105 | 16 | 0.008128 |  | 0.008128 | 0.008128 | 0.016256 | 0.024384 | 0.024384
| 14 | 0.00515 |  | 194.1748 | 194.1748 | 97.0874 | 64.7249 | 64.7249 | 14 | 0.00515 |  | 0.00515 | 0.00515 | 0.0103 | 0.01545 | 0.01545
| 13 | 0.004084 |  | 244.858 | 244.858 | 122.429 | 81.6193 | 81.6193 | 13 | 0.004084 |  | 0.004084 | 0.004084 | 0.008168 | 0.012252 | 0.012252
| 11 | 0.002568 |  | 389.4081 | 389.4081 | 194.704 | 129.8027 | 129.8027 | 11 | 0.002568 |  | 0.002568 | 0.002568 | 0.005136 | 0.007704 | 0.007704
| RAYLUX - White-Light |  | Lamp Current | RL25 | RL50-AI | RL100-AI | RL200-AI | RL300-AI | RAYLUX - White-Light |  | Lamp Current | RL25 | RL50-AI | RL100-AI | RL200-AI | RL300-AI
|  |  | Per Panel - amps: | 1 Panel @ 0.7 | 2 Panels @ 0.7 | 2 Panels @ 1.4 | 2 Panels @ 2.1 | 3 Panels @ 2.1 |  |  | Per Panel - amps: | 1 Panel @ 0.7 | 2 Panels @ 0.7 | 2 Panels @ 1.4 | 2 Panels @ 2.1 | 3 Panels @ 2.1
| Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.7 | 1.4 | 2.8 | 4.2 | 6.3 | Nominal Wire | Total 2-Core Cable | Total Lamp - amps: | 0.7 | 1.4 | 2.8 | 4.2 | 6.3
| AWG | Resistance - Ohms/ft |  |  | Max Cable Runs - feet |  |  |  | AWG | Resistance - Ohms/ft |  |  | Voltage drop per foot - maximum voltage drop allowed = 0.6V
| 20 | 0.0207 |  | 41.4079 | 41.4079 | 20.7039 | 13.8026 | 13.8026 | 20 | 0.0207 |  | 0.02415 | 0.02415 | 0.0483 | 0.07245 | 0.07245
| 18 | 0.01302 |  | 65.8328 | 65.8328 | 32.9164 | 21.9443 | 21.9443 | 18 | 0.01302 |  | 0.01519 | 0.01519 | 0.03038 | 0.04557 | 0.04557
| 16 | 0.008128 |  | 105.4556 | 105.4556 | 52.7278 | 35.1519 | 35.1519 | 16 | 0.008128 |  | 0.0094827 | 0.0094827 | 0.018965 | 0.028448 | 0.028448
| 14 | 0.00515 |  | 166.4355 | 166.4355 | 83.2178 | 55.4785 | 55.4785 | 14 | 0.00515 |  | 0.0060083 | 0.0060083 | 0.012017 | 0.018025 | 0.018025
| 13 | 0.004084 |  | 209.8783 | 209.8783 | 104.9391 | 69.9594 | 69.9594 | 13 | 0.004084 |  | 0.0047647 | 0.0047647 | 0.0095293 | 0.014294 | 0.014294
| 11 | 0.002568 |  | 333.7784 | 333.7784 | 166.8892 | 111.2595 | 111.2595 | 11 | 0.002568 |  | 0.002996 | 0.002996 | 0.005992 | 0.008988 | 0.008988
There are internal adjustments available within the PSU to increase the above distances by upto 50%.
Contact Raytec technical support for advice.
| UK/Europe/Middle East | +44 (0) 1670 520 055 | Americas | + 1 613 270 9990